## Sheet1
source | target | Verify | Condition
blower motor no start | M1-AC fail open | check motor contactor
exceed motor FLA | bad bearings | check motor bearings
exceed motor FLA | binding in blower section | check for obstruction
F4 Output 1A FO | loose circuit board | check for loose board
F4 Output 1A FO | Incorrect F4 Profile | check F4 Program
F4 Output 1B FC | defective | check function
F4 Output 1B FC | loose circuit board | check for loose board
F4 Output 1B FO | loose circuit board | check for loose board
F4 Output 1B FO | defective | check function
F4 SP OVR Limit | operator error | check F4 Program
failed t/c input | wrong t/c type | verify correct t/c
failed t/c input | loose t/c connect | check t.c terminals
flow restriction | excessive bend | kinked hose/tubing
flow restriction | debris | check for obstruction
high/low limit ctrl relay FO | Incorrect controller configuration | verify controller settings
high/low limit ctrl relay FO | incorrect t/c input | false t/c reading
HTR Fuse/Breaker Trip | HTR short | inspect HTRs
HTR Fuse/Breaker Trip | bad fuse | check fuses
HTR short | Component EOL | inspect for EOL
HTR short | loose htr element | check fasteners
ice on blower | defrost fail | verify defrost function
Incorrect F4 Profile | operator error | check F4 Program
Incorrect F4 Profile | controller reset | default reset
Incorrect F4 Profile | operator error | check F4 Program
failed t/c input | wrong t/c type
loose circuit board | TCU Vibration | vibration
M1-AC fail open | defective | check function
M1-AC fail open | M1-OVR fail open | check M1-OVR fail open
M1-AC fail open | high/low limit ctrl relay FO | check relay closed between high/low limits
M1-OVR fail open | exceed motor FLA | check motor amperage draw
No 120VAC power | XFMR fail | check transformer
No 120VAC power | unit 120VAC fuse/breaker trip | check unit power fuses
No 120VAC power | XFMR source fuses/breaker | check fuses/breaker
No 480VAC power | facility 480VAC source fail | check facility source
No 480VAC power | unit 480VAC fuse/breaker trip | check unit power fuses
TCU Failed Cooling | Incorrect F4 Profile | check F4 Program
TCU Failed Cooling | F4 Output 1B FC | verify 1B function
TCU Failed Cooling | SV-1 LN2 FC | verify SV-1 function
TCU Failed Cooling | SV-2 LN2 FC | verify SV-2 function
TCU Failed Heating | HTR Fuse/Breaker Trip | check fuses | TBD
TCU Failed Heating | F4 Output 1B FO | verify 1B function | F4 output function check
TCU Failed Heating | TS-1 OVR TEMP | check settings
TCU Failed Heating | SSR-1 Fail Open | bench check SSR
TCU Failed Heating | SSR-2 Fail Open | bench check SSR
TCU Failed Heating | SV-2 LN2 FO | verify SV-2 function
TCU Failed Heating | SW2 Fail Open | check switch
SSR-1 Fail Open | defective | check function
SSR-2 Fail Open | defective | check function
SV-1 LN2 FC | flow restriction | check for debris
SV-2 LN2 FC | flow restriction | check for debris
SV-2 LN2 FO | debris | check for obstruction
Temperature Control Unit | TCU Failed Heating | EMR Condition
Temperature Control Unit | TCU Failed Cooling | EMR Condition
Temperature Control Unit | No 480VAC power | EMR Condition
Temperature Control Unit | No 120VAC power | EMR Condition
Temperature Control Unit | blower motor no start | EMR Condition
TS-1 OVR TEMP | failed t/c input | correct t/c ? | N/A
TS-1 OVR TEMP | fail close | verify TS-1 function | TS-1 Function Check
TS-1 OVR TEMP | F4 SP OVR Limit | verify F4 set point
TS-1 OVR TEMP | Flow Restriction (kinked hose) | kinked hose/tubing
TCU Vibration | ice on blower | imbalanced blower
TCU Vibration | loose blower | check fasteners
XFMR fail | defective | check X1 - X4 voltage
defective | Component EOL | EOL
defective | MFR Error | warranty
Temperature Control Unit | No Communication | EMR Condition
No Communication (RS-485) | RS-485 fail | TBD
defrost fail | defrost timer relay fail | check timer relay
defrost fail | defrost limit ctrl fail | verify ctrl settings
defrost timer relay fail | defective | EOL
defrost timer relay fail | incorrect timer settings | check settings
RS-485 fail | Bad cable | check cable
bad cable | defective | discard
RS-485 fail | Controller RS-485 fail | check com
controller RS-485 fail | defective | check HW
controller RS-485 fail | incorrect RS-485 settings | check settings
RS-485 fail | PC RS-485 fail | check com
PC RS-485 fail | incorrect RS-485 settings | check settings
PC RS-485 fail | defective | check HW
operator error | no training | TBD
operator error | procedure not followed | TBD
TCU Failed Cooling | No LN2 Source | check LN2 system
No LN2 Source | Low LN2 Pressure | check LN2 tank pressure/lvl
No LN2 Source | LN2 leak | check for local LN2 leak
TCU Failed Heating | F4 Output 1A FO | verify 1A function
No 480VAC power | incorrect unit pwr cable | check terminals and amp rating
loose htr element | defective
loose htr element | TCU Vibration
LN2 leak | Internal LN2 leak
LN2 leak | External LN2 leak
Temperature Control Unit | Scheduled Maintenance | Preventive Maintenance
Scheduled Maintenance | Unit PM
Scheduled Maintenance | Unit config change
Unit config change | component upgrade
Unit config change | test specific modification
test specific modification | PWR cable 30A to 60A
test specific modification | PWR cable 60A to 30A
loose blower | defective belt | inspect belt
SV-2 LN2 FC | defective | replace
Temperature Control Unit | TCU Mechanical | EMR Condition
TCU Mechanical | blower motor bearings | vibration
TCU Mechanical | drive belt | vibration
blower motor bearings | defective | inspect bearings
drive belt | defective | inspect belt

## Sheet2
Slow Heat | HTR Fuse/Breaker Trip | check fuses/breaker
Slow Heat | F4 Output 1B FO | check function | FC relay out keeps SV-2 open; dumping LN2 into the chamber.
Slow Heat | SV-2 LN2 FO | verify SV-2 function | FO SV-2 open; dumping LN2 into the chamber.
Slow Cold | Low LN2 Pressure | check Nitrogen pressure
Slow Cold | flow restriction | restriction of LN2 flow
Slow Cold | F4 Output 1A FC | inadvertant heating